## Slide 1
Data Centers

## Slide 2: Data Centers
What is a datacenter?
  “ a data center is a place where you keep machines that are a shared resource”
  Other terms that basically mean the same thing
    Server room
    Machine room
    Server closet
  Many things that make a data center more than just another room where computers run

## Slide 3: Major Components to a Data Center
What makes a data center more than just a closet with a bunch of servers?
    Location
    Access
    Security
    Power, Cooling, Humidity
    Fire Suppression
    Racks
    Cable Management
    Communications
    Console Access
    Workbench
    Tools, parts, etc

## Slide 4: Location
Where is your data center going to be located? How many do you need?
Large multi-national corporations may have many with one acting as a primary and others as a backup
May run data centers concurrently as to balance load and provide immediate fail-over
Smaller companies or educational institutions may have many, one for each college, or a few for the entire university
May be placed ‘strategically’ around the university or around the area (CNY) as to minimize expense.
Even the best data centers with redundant power, cooling, etc. can fall victim to a contactor with a backhoe or excavating equipment.

## Slide 5: Location
If your area is susceptible to flooding, don’t put your data center in the basement.
“Some company has two data centers. They change primary data centers every 6 months.”
Why?
Florida is susceptible to hurricanes and Colorado is susceptible to huge snow storms.
Also a great way of testing their disaster recovery environment.

## Slide 6: Access
What type of access is required?
  Wheelchair, ramps, loading docks to unload equipment?
Some equipment is wider than the average sized door. Need double-doors.
Restrict access to people who don’t need it.

## Slide 7: Security
What type of security do you require?
  Numeric key pads – bad idea. Anyone can share the code. No way of knowing who came in.
  Keys, - better, at least you know who you gave the key to originally
  Card swipes – even better, logs entry information and controls access
  Proximity detectors – better still, same advantages as card swipes but more convenient
  Biometrics – almost there. Thumb print reader or voice recognition. Disadvantages ?
  Two Factor, -best, something you have and something you know. A numeric keypad that requires both a static or non-changing code and a one-time-password security token.

## Slide 8: Cooling
For every watt of power used in the data center, you need to plan for the same amount of power to cool your equipment.
Direct your cool air where you need it
New types of cooling concepts, “cool the servers, not the entire room”
Rear door heat exchangers. Cools only the servers and not surrounding room air. Most efficient.

## Slide 9: Large Data Center Air Conditioner and Rear Door Heat Exchanger

## Slide 10: Hot and Cold Isles and Humidity
Cold air goes in front of rack, heated by server, exited out back.
Arrange your data center so the backs of the racks are towards each other. This forms hot and cold isles.
Easier to collect the hot air. Heat rises.
Keep server room humidity between 45% - 55%. Too low, static, too high, condensation.

## Slide 11: Power
Multiple sources of electricity.
  Multiple feeds from multiple substations.
  Generator, not only for emergencies but also for normal operations.
  What type of power does it produce, do you need? 110V, 220V, 480V?

## Slide 12: Power
Do you have a Uninterruptable power supply (UPS)? How big?
How long does it need to last, 10 minutes, 1 hour, 4 hours?
Varies depending if you have a generator or not.
Do you have automatic transfer switches, (ATM)?
  Switches that ‘sense’ if line power or in Syracuse, National Grid power if present, and if not, automatically starts generator and transfers load. When line power returns, shuts off generator and returns load to line power.

## Slide 13: Power Distribution Unit (PDU)
Looks like a power strip, much more.
Can be horizontally or virtually mounted
Monitor, record, and control each outlet remotely via network.
Should have two per server, one connected to line power and one connected to UPS / Generator power

## Slide 14: Monitor your Power

## Slide 15: Fire Suppression
Require Fire suppression methods, required by law /code
Conventional (Water and Sprinklers) = Bad
Many other methods
  CO2, good for servers, bad for people
  Conventional extinguishers
  Consult local fire authorities

## Slide 16: Racks
The ‘spine’ of the data center
Dictate other components
  Wiring, cooling, power, etc
  Not inexpensive, up to $10,000 per rack with required products (power, cooling, networking, etc)
Standard 19” wide, width of standard mountable equipment. 19” between posts.
Some telecomm equipment is wider. Special order racks available or equipment comes with these racks already.
May purchase racks wider and deeper than your needs as to leave room for networking, power, cooling, etc.
2 or 4 posts
  4 is better but more expensive.
Rack equipment in U’s or rack units,
  1.75 inches per “U”
  Can use square nuts or screws to mount equipment

## Slide 17: Rack Cooling
Racks are typically open at the bottom to allow cool air to flow in.
Heat rises exits out the back
Not a location to run wires. Run cabling overhead with above-the-racks wire trays
If keep doors and sides on if using raised floor, off it using standard air-conditioning
Monitor temperature inside racks
We use device called “Weather Goose”

## Slide 18: Racks Determine Cable Management
A good cabling job is a pleasure to work with.
Don’t ‘build-your-own’ cables. Purchase cat6 or category 6 cables.
Purchase special cable management products.
Easily identify which cable connects to what.
Color code or label your cables
Separate power from network cables. Power down one side, network cables down the other

## Slide 19: Cable Management Images

## Slide 20: Our Guidelines

## Slide 21: Communications
Put a telephone in your server room incase you need to call someone in for assistance or be speaking with a vendor while standing in front of the server.
“Bridge” the telephone line into a infrequently used circuit to save money.
Don’t rely on cell phones. Can be difficult to hear plus more interference in server room.

## Slide 22: Console Access
KVM usage
  A KVM switch is a hardware device that allows a user to control multiple computers from one or more sets of keyboards, video monitors, and mice.
If no KVM or out-of-band management, consider using a ‘crash cart’ or setup cart.
  Basically a vertical cart with a keyboard, mouse, and monitor used when 1st setting up servers or if they crash so bad you can’t use other management techniques

## Slide 23: Workbench, Tools, Parts
Have a place where your staff can test out or ‘burn in’ a server before putting it into production.
Place to troubleshoot failed servers
Have extra patch cables, nuts, bolts, “spare parts” on hand.

## Slide 24: Summary
Data center is much more than a standard room or closet.
Many things make a server room unique.
Look for alternatives, outsource
If you are going to build it, do it right the first time.